
        Hoyer


Industrial Delivery Site Hazard Checklist

1. Customer Information:


	Customer: NOLAN OILS
	Ship to No:
	Products: 

	Location: BUCKNELL ROAD
 MIDDLETON  STONEY 
	
	Contact person: Mr  M Nolan
                 01869/342114


Tank Information:


	Tank No or Letter
	Product


	Capacity (litre)


	 


	1 
	DERV
	105.011
	
TWO   TANKS  LINKED

	2
	GAS/OIL
	157.484
	
TWO   TANKS  LINKED

	3 & 4
	KERO
	296.947
	         THREE  TANKS  LINKED


2. Hazard Checklist:
	Assessment Items
	Yes
	No


	N/A


	Remarks/Recommendations


	Is backing or excessive maneuvering required to get into the site ?

	
	  NO
	
	

	Is backing or excessive maneuvering required to get to the Fill Pipes ? Can Fill Pipes be reached with the standard hose pack ?
	
	NO
	
	

	Are there any vehicle height restrictions ?


	
	NO
	
	Height limit:                    Meters.

	Are there any vehicle weight restrictions ?


	YES
	
	
	Weight limit:                   GVW  
       SEE  ROUTE CARD

	Area there any vehicle length restrictions ?


	
	NO
	
	Length limit:                   Meters

	Is backing or excessive maneuvering required to get off the site ?

	
	NO
	
	

	Is the Driver working area free of frequently moving heavy vehicles and forklifts ?


	YES
	
	
	

	Is Driver working area free of slip, trip and fall hazards ?


	YES
	
	
	


	Assessment Items
	Yes
	No


	N/A


	Remarks/Recommendations


	Any other hazards in the Driver working area ?


	
	NO
	
	

	If there is more than one Storage Tank at the location is each tank AND Fill Pipe uniquely identified with a legible number of letter ?
	YES
	
	
	

	Are the Storage Tanks bunded ? If so is the bund big enough for the tank contents plus 10% ?


	YES
	
	
	

	Are the Storage Tank areas free of debris and vegetation ?


	YES
	
	
	

	Are the Storage Tanks and their Fill Pipes free of leaks ? Does equipment maintenance look acceptable ? 
	YES
	
	
	

	Do the Storage Tanks have a working contents gauge ? Drivers must not climb onto tanks or into bunds to view gauges 
	YES
	
	
	FUELMASTER  TANK GAUGING

ALARM PANEL FITTED

	Do Storage Tank Vent Pipes seem to be clear and face away from Driver working area ?


	YES
	
	
	

	Are all Storage Tank and Fill Pipes fitted with Grade Labels ?


	YES
	
	
	

	Does each Fill Pipe have a Gate Valve and Non- Return Valve fitted close to the connection ?

 
	YES
	
	
	

	Is a pump required to fill the Storage Tank ? 


	
	
	
	TANKS CAN BE FILLED BY VEHICLE PUMP OR CUSTOMERS OWN  STRIPPER PUMP

	What are the Fill Pipe sizes and what fittings are required ?


	
	
	
	ALL FITTINGS ARE 4 INCH             CAMLOCK

	Is the lighting sufficient to allow for safe deliveries during darkness hours ?


	YES
	
	
	YES GOOD LIGHTING AS NIGHT DELIVERIES ARE REQUIRED


	Assessors  Name
	D  HACKETT

	Signature


	

	Date of Assessment


	17/06/04



Sketch of site including entrance, route to discharge area and exit from site

Due to the concerns raised regarding this delivery I have visited  Nolan Oils to check out the points raised.

1 That no overfill protection alarms are fitted to the tanks.

       Site visit has reveled that overfill protection is fitted to all tanks which is activated when tanks are filled to 97% and this is an audible Alarm.
The driver has the means to check the tank ullages on the fuelmaster control panel for each tank and also the audible overfill prevention alarm on each tank.
2 Stream running at rear of storage tanks
Site visit has reveled that this is in fact a small pond and that all the necessary precautions have been taken if a spillage or overfill was to occur.

Nolan oils have had a new interceptor system installed to insure that the pond would not be contaminated. The driver is required to close a valve on the interceptor in the event of an EMERGENCY.

3 No Showers or toilet facilities 

      As all office buildings are closed and alarmed at night access to the toilets is not available.
       4               Security for Driver through out the delivery

From the time the driver enters the site his movements are monitored on CCTV Security Cameras

Cameras are monitored through out the night by trained security
Staff at all times

                                                     Recommendation 

Night deliveries only one vehicle to off load at a time, and all night deliveries to use customers stripper pump.
                                                 Reason for this to be carried out.
Vehicle would have to reverse in and this would put the driver out of view to the CCTV CAMERA through out the delivery.




























































STOPS SECTION 2: Risk Assessment 
EXXONMOBIL CUSTOMER SERVICE
PAGE 2.5
April 2000

